## Slide 1
DATA CENTRE / WASTE HEAT
Heat that would
otherwise be lost
How a data centre could warm a public pool and a district-heating network
Engineering research • MATLAB / Simulink • 2025 scenario
23 OCT 2026

## Slide 2
DATA CENTRE / HEAT REUSE
01
PROJECT GLOSSARY · 1/2
Six terms that make the rest readable
Servers produce heat; we study how it can be used safely.
2025 model · research, not site measurements
23.10.2026
Data centre
A facility with servers, networking, power and cooling.
IT load
Server electrical demand; this study assumes a 10 MW peak.
Waste heat
Heat that must be removed from operating equipment.
Coolant loop
Pipes, pumps and fluid used to transport heat.
Heat exchanger
Transfers heat between hydraulically isolated fluid streams.
District heating
A hot-water network distributing heat to buildings.

## Slide 3
DATA CENTRE / HEAT REUSE
02
PROJECT GLOSSARY · 2/2
How it delivers heat and handles failures
Some terms describe efficiency; others describe IT safety.
2025 model · research, not site measurements
23.10.2026
Heat recovery
Reusing heat that would otherwise be rejected.
Heat pump (HP)
Uses electricity to raise heat to a usable temperature.
Thermal store (TES)
Stores heat to smooth supply and demand over time.
Backup boiler
Provides heat when recovery and storage cannot cover demand.
N+1 redundancy
Adds one standby unit to the number required in normal operation.
SCADA
Supervisory monitoring and control: values, alarms and trends.
Key distinction: 1 MW is power; 1 MWh is the energy delivered at 1 MW for one hour.

## Slide 4
DATA CENTRE / HEAT REUSE
03
VARIABLE PASSPORT · 1/2
Six quantities used in diagrams and plots
MW denotes power, °C denotes temperature. MWh instead measures energy.
2025 model · research, not site measurements
23.10.2026
SYMBOL
UNIT
MEANING AND DATA ORIGIN
P_IT
MW
Server electrical input; load profile is modeled.
Q_avail
MW
Server heat available for recovery; modeled, not metered.
Q_pool
MW
Useful pool heating, including any heat-pump contribution.
Q_DH
MW
Useful heat-pump output delivered to district heating.
P_HP
MW
Electric input power to the heat-pump compressor.
T_pool
°C
Pool-water temperature; simulated, not measured.
For a heat pump: useful heat = extracted source heat + compressor electricity.

## Slide 5
DATA CENTRE / HEAT REUSE
04
VARIABLE PASSPORT · 2/2
Annual energy and efficiency indicators
An absent ERF is deliberate: it cannot be reported as measured without meters.
2025 model · research, not site measurements
23.10.2026
SYMBOL
UNIT
MEANING AND DATA ORIGIN
E_IT
MWh
IT energy over a period; derived from the model load.
E_DC
MWh
Total facility energy, including cooling and other overhead; estimated.
E_src
MWh
Annual extracted server heat; this is not the regulated ERF.
COP
1
Useful heat output per unit of compressor electricity.
PUE
1
E_DC / E_IT; 1.36 is an assumption, not a site measurement.
ERF
1
Energy reuse factor at the DC boundary; site metering is missing.
Evidence: ASSUMED (10 MW, PUE) · SIMULATED (Simulink) · UNMEASURED (ERF, real COP).

## Slide 6
DATA CENTRE / HEAT REUSE
05
THE PROBLEM
Servers do more than compute
Almost all electricity used by servers eventually becomes heat.
2025 model · research, not site measurements
23.10.2026
10 MW
assumed maximum
IT load
Servers must be cooled 24/7
Even when the pool and the city need no heat.
The usual path — reject the heat outdoors
Our question: how much can be reused without compromising IT safety?

## Slide 7
DATA CENTRE / HEAT REUSE
06
CONCEPT
One idea: give the heat a second destination
Not instead of IT cooling, but alongside it.
2025 model · research, not site measurements
23.10.2026
01
Data centre
Warms technical coolant
02
Heat recovery
Transfers heat across isolated loops
03
Useful heating
Pool + district network
Backup cooling remains independent of heat sales.

## Slide 8
DATA CENTRE / HEAT REUSE
07
ARCHITECTURE
The system at a glance
Recover available server heat first; dispatch it to where it is needed.
2025 model · research, not site measurements
23.10.2026
Servers / cooling
Heat recovery loop
Heat pump → district heating
Heat exchanger → pool
Independent IT backup cooling
IT cooling must continue even if heat reuse or the network stops.

## Slide 9
DATA CENTRE / HEAT REUSE
08
ANNUAL BALANCE
What the simulated year shows
Server heat splits into recovered energy and energy rejected outdoors.
2025 model · research, not site measurements
23.10.2026
71.8
GWh of IT heat per year
38.3
GWh recovered
33.6
GWh rejected
This is a simulated energy balance, not a reportable measured ERF.

## Slide 10
DATA CENTRE / HEAT REUSE
09
MODEL INPUTS
Where the numbers come from
Strength: reproducible calculations. Limitation: no operating-site telemetry.
2025 model · research, not site measurements
23.10.2026
Weather: external dataset
NASA POWER • Bratislava • 8,760 hours in 2025. Gridded reanalysis.
IT servers: assumed load
Load and recoverable fraction are model assumptions, not meter readings.
Physics: MATLAB / Simulink
Heat source, pool, heat pumps, storage and gas backup in 5-minute steps.
Verification: independent QA
Balance checks on 420,480 samples across four annual scenarios.

## Slide 11
DATA CENTRE / HEAT REUSE
10
WEATHER AND DEMAND
Demand changes sharply with the season
District heat demand is calculated from Bratislava hourly outdoor temperature in 2025.
2025 model · research, not site measurements
23.10.2026
1
2
3
4
5
6
7
8
9
10
11
12
Monthly district-heat demand
9.0
0
thousand MWh

## Slide 12
DATA CENTRE / HEAT REUSE
11
DISTRICT HEATING
How the heating demand is supplied
The heat pump supplies most of the heat; backup gas covers shortages and peaks.
2025 model · research, not site measurements
23.10.2026
56.8
GWh district demand
47.8
GWh useful HP heat
9.19
GWh backup gas heat
Heat pump
Backup gas
The storage tank shifts heat across time, so summed production flows include charge/discharge effects.

## Slide 13
DATA CENTRE / HEAT REUSE
12
A PRACTICAL EXAMPLE
A swimming pool makes the benefit tangible
Assumed 25 × 12.5 × 1.6 m dimensions are a study scenario, not a universal pool standard.
2025 model · research, not site measurements
23.10.2026
25 × 12.5 × 1.6 m
500 m³
water volume
150 kW
heating capacity
250
MWh heat per year
27.62 °C
modeled peak

## Slide 14
DATA CENTRE / HEAT REUSE
13
POOL PHYSICS
Where pool heat is gained and lost
The model includes water heat capacity, evaporation, convection, radiation and makeup water.
2025 model · research, not site measurements
23.10.2026
Temperature change
ΔT = (Qin − Qloss) · Δt / (ρ · V · cp)
Qin: heat added
Qloss: heat lost
V: water volume
A pool cover reduces evaporation, and therefore heat demand.

## Slide 15
DATA CENTRE / HEAT REUSE
14
TWO OPERATING MODES
35°C: direct. 25°C: via a heat pump
The available coolant temperature determines which equipment is practical.
2025 model · research, not site measurements
23.10.2026
35 °C
Direct transfer
Servers
Pool
No dedicated pool compressor if the exchanger achieves the required heat transfer.
25 °C
Heat pump
Source
Compressor → pool
Compressor electricity is needed; COP=4 is assumed, not manufacturer-certified.

## Slide 16
DATA CENTRE / HEAT REUSE
15
ENERGY ACCOUNTING
A heat pump does not create energy
At 25°C the recovered source supplies heat; electricity drives the compressor.
2025 model · research, not site measurements
23.10.2026
187.6 MWh
62.5
Recovered server heat
Compressor electricity
= 250.1 MWh
useful pool heating over one year

## Slide 17
DATA CENTRE / HEAT REUSE
16
DISTRICT HEAT PUMP
Why COP matters
COP measures useful heat delivered per unit of compressor electricity.
2025 model · research, not site measurements
23.10.2026
COP ≈ 4.90
calculated from a synthetic Carnot approximation
47.8 GWh
district useful heat
9.74 GWh
compressor electricity
OEM certification is required at the actual 25–35°C source and 70°C sink conditions.

## Slide 18
DATA CENTRE / HEAT REUSE
17
EQUIPMENT
The equipment we would need
This is a technical selection brief, not a purchase-ready bill of materials.
2025 model · research, not site measurements
23.10.2026
Pool: plate heat exchanger
150 kW; ≈25 m² at 35/32 ↔ 27.5/29.5°C with assumed heat transfer coefficient.
District network: modular HPs
Carrier or Oilon; module count requires OEM output/COP data for our temperatures.
Pumps and metering
Preliminary 43.2 m³/h primary and 64.8 m³/h pool-side flow.
Independent IT heat rejection
Full 10 MW rejection even with no heat customers, with N+1 resilience.

## Slide 19
DATA CENTRE / HEAT REUSE
18
CATALOGUE CHECK
A 1.57 MW rating is not a site guarantee
A manufacturer rating refers to specific test temperatures, not every operating point.
2025 model · research, not site measurements
23.10.2026
1.57 MW
Carrier 61XWH-ZE17: published nominal point
6 + 1
nominal units for 9.42 MW + one spare
Published test point: 20/15°C source → 70/75°C sink.
For the intended 35/30°C → 50/70°C operation, OEM selection is still required. 6+1 is not a purchase decision.

## Slide 20
DATA CENTRE / HEAT REUSE
19
CAPACITY CHOICE
Why the biggest plant is not automatically best
Compare peak hours, underused capacity and backup-gas substitution.
2025 model · research, not site measurements
23.10.2026
6 MW
10,303 MWh
8 MW
2,564 MWh
10 MW
2.74 MWh
12 MW
0 MWh
Extra annual backup-gas heat with constrained HP capacity

## Slide 21
DATA CENTRE / HEAT REUSE
20
POOL ECONOMICS
The simpler route currently wins on cost
Against separate gas-boiler pool heating at Eurostat Slovakia 2025 benchmark prices.
2025 model · research, not site measurements
23.10.2026
€12,307
annual energy OPEX advantage: direct HX
€4,280
annual energy OPEX advantage: pool heat pump (COP=4 assumed)
Excludes installed CAPEX, maintenance, hall HVAC and actual contracted tariffs.

## Slide 22
DATA CENTRE / HEAT REUSE
21
INVESTMENT DECISION
Installed cost can change the conclusion
Direct HX: 20-year NPV at 6% discount. These are budget scenarios, not supplier quotations.
2025 model · research, not site measurements
23.10.2026
€45k
NPV +€71k
€75k
NPV +€34k
€110k
NPV €-9k
Under the model assumptions, break-even installed CAPEX is around €103k.

## Slide 23
DATA CENTRE / HEAT REUSE
22
TEMPERATURE AND SAFETY
Comfort and a strict temperature boundary
The simulation deliberately stays below the published upper temperature limit.
2025 model · research, not site measurements
23.10.2026
27.25
27.60
27.80
28.00
27.62 °C
annual maximum in Simulink
Actual sensor errors, valve overshoot and effective legal text still require testing.

## Slide 24
DATA CENTRE / HEAT REUSE
23
RESILIENCE
What if nobody accepts the heat?
Servers cannot depend on pool schedules or district heating demand.
2025 model · research, not site measurements
23.10.2026
10 MW
full-rated independent IT heat rejection required
1,727 m³/h
at a 5 K water temperature difference
N+1
survive failure of at least one unit
Thermal storage is not coolant flow: pumps require UPS and redundancy.

## Slide 25
DATA CENTRE / HEAT REUSE
24
FAULT SCENARIOS
A useful model must reveal unsafe conditions
Independent cooling model: six one-hour tests at 5-second intervals, with a 10 m³ buffer.
2025 model · research, not site measurements
23.10.2026
Spare starts in 30 sec
Within limit
Spare delayed 5 min
Overheat detected
Capacity derated in heat
Capacity shortage flagged
Coolant pump failure
No coolant flow — trip
Unsafe cases are successful hazard detections, not successful safe operation.

## Slide 26
DATA CENTRE / HEAT REUSE
25
EVIDENCE AND STANDARDS
Verified model ≠ certified facility
We mapped standards but have not signed off compliance without full texts and tests.
2025 model · research, not site measurements
23.10.2026
34
defined KPIs
56
standards checkpoints
36
use cases
14
defined signals
22 / 36
passed software checks
14
remain blocked
PUE=1.36 is assumed. Reportable ERF and WUE require meters.

## Slide 27
DATA CENTRE / HEAT REUSE
26
USE CASES
What different people gain
Visitors notice a warm pool; operators need a safe, measurable heat system.
2025 model · research, not site measurements
23.10.2026
Pool visitor
Comfortable water and potentially lower energy costs.
Pool operator
Heat forecast, water-temperature control and backup operation.
Data-centre operator
Recover heat without depending on external customers for IT cooling.
District network / city
An additional heat source, with reduced modeled backup-gas reliance.

## Slide 28
DATA CENTRE / HEAT REUSE
27
NEXT STEPS
From research to a buildable design
The project needs staged evidence, not a leap from simulations to purchasing.
2025 model · research, not site measurements
23.10.2026
01 · Measure
IT loads, coolant temperatures/flows and facility energy
02 · Select
Heat pumps and HX from confirmed operating-point curves
03 · Engineer
Hydraulics, UPS, independent backup cooling and safeguards
04 · Validate
Fault testing, applicable standards and acceptance
Buying equipment before OEM ratings and safety testing would be premature.

## Slide 29
DATA CENTRE / HEAT REUSE
What the study shows
Server heat can be allocated among multiple useful destinations.
At a 35°C source, direct pool heating appears simpler and cheaper than a separate HP.
Heat reuse must never become the only IT cooling route.
A research conclusion, not an installation approval.

## Slide 30
DATA CENTRE / HEAT REUSE
28
REFERENCE
How to interpret every number in this deck
All major numbers come from saved model results with explicit evidence limits.
2025 model · research, not site measurements
23.10.2026
CALCULATED
2025 model, 8,760 hours, 300-second Simulink, independent balance QA.
ASSUMED
10 MW IT, PUE=1.36, modeled COP, equipment budgets, 500 m³ pool.
STILL UNVERIFIED
OEM duty/COP, site measurements, physical safety and licensed standards.
PRIMARY SOURCES
NASA POWER • Eurostat SK • Carrier / Eurovent • EU 2024/1364 • STN EN 15288.
Supporting files: MATLAB/Simulink, KPI CSV/JSON, 56 standards checkpoints, 36 use cases and QA.